## Clear Openings
Single Door Width & Clear Opening From Frame Width |  |  |  | Frame Width & Clear Opening From Double Door Width |  |  |  | Variables |  |  | Minimum Door Widths
| Fire Rating* | FD30 |  | Fire Rating* |  | FD30 | Fire Rating | FD30 |  |  | Leaf Width | 300
| Frame Width | 994 |  | Door Width 1 |  | 724 | Opening Angle (°) | 90 |  |  | Leaf Thickness | 44 | NFR
| Door Thickness* | 44 |  | Door Width 2 |  | 724 | Stop Width | 15 |  |  | Leading Edge | 3 | FD30
| Jamb Thickness LH* | 32 |  | Door Thickness* |  | 44 | Door Thickness | 44 | Parameters - Do Not Alter |  | Hinge Offet* | 8 | FD60
| Jamb Thickness RH* | 32 |  | Jamb Thickness - LH* |  | 32 | Jamb Thickness - LH | 32 |  |  | Door Gap | 3 | FD90
| Stop Width* | 15 |  | Jamb Thickness - RH* |  | 32 | Jamb Thickness - RH | 32 |  |  | Door Width With Leading Edge | 297.6941 | FD120
| Door Side Clearance* | 3 |  |  | Door Side Clearance* | 3 | Door Side Clearance | 3 |  |  | Door Opening Radius | 303.6792
Door Width |  | 924 |  | Frame Width |  | 1521 | Hinge Width | 76 |  |  | Available opening | 304.5
Clear Opening (1) |  | 861.4784 |  | Clear Opening (1) |  | 1349.9567 | Hinge Rebate Widthin Frame | 30 |  |  | Theoretical Clearance | 0.82075
|  |  | * - Do NOT Alter These Values |  |  |  | Frame To Knuckle Centre Dim | 8 |  |  | Does Door Clear Frame | YES!
|  |  | (1) - Door Angle At 90° & Above & No Projecting Ironmongery |  |  |  | Opening Radius Inside Edge Of Door | 52.0216
[7 empty] | Length To Subtract From Frame Internal Width | 53.5216 |  | * Std Hinge Offset = 8mm
Frame Width & Clear Opening From Single Door Width |  |  |  | Clear Opening From Frame Width & Primary Leaf Width
| Fire Rating* | FD30 |  | Fire Rating* |  | FD30
| Door Width | 1175 |  | Primary Leaf Width |  | 924
| Door Thickness* | 44 |  | Frame Width |  | 1510
| Jamb Thickness - LH* | 32 |  | Door Thickness* |  | 44
| Jamb Thickness - RH* | 32 |  | Jamb Thickness - LH* |  | 32
| Stop Width* | 15 |  | Jamb Thickness - RH* |  | 32
| Door Side Clearance* | 3 |  |  | Door Side Clearance* | 3
Frame Width |  | 1245 |  | Secondary Leaf Width |  | 513
Clear Opening (1) |  | 1112.4784 |  | Primary Leaf Clear Opening (1) |  | 876.4784